## Phasor_Applications Subset
Note that yellow filled cells are cells with best/initial guesses by the author and are unsubstantiated. Unfilled/white-filled cells have received some feedback/guidance, but more is always welcomed. Comments denote contributors.
Phasor Measurement Unit Application Data Requirements
| PMU Measurement Parameters |  |  |  |  | Delay/Quality Parameters |  |  |  | Other Information
Application | Amplitude, Angle, or Frequency Precision (p.u., degrees, mHz) | Amplitude, Angle, or Frequency Accuracy (%, absolute values) | ROCOF (Hz/s) | Frequency Range (Hz) | Time Accuracy (ms) | Measurement Transfer Time (ms) | Message Rate (Reports/sec) | Time Window (sec) | Data Loss Sensitivity (Reports or ms) | Performance Class (M/P/X/N) | Tools /Platforms | Comments
Small-Signal Stability Monitoring | 0.5 degrees 0.01 Hz | TVE | STD | 0.1 - 1.0 Hz | STD | 50 ms | 60 Reports/sec | 600 seconds | 10000 ms | M | EPG RTDMS, Allstom eTerra Vision | Even in real-time applications, small-signal stability often requires a long analysis window (unless event-based). Data drop outs can be tolerated and "burst data" packets can be handled by many algorithms.
Voltage Stability Monitoring/Assessment | 0.01 p.u. mag 0.5 degrees | TVE | STD | 0.1 - 10.0 Hz | STD | 500 ms | 30 Reports/sec | 300 seconds | 10000 ms | X | EPG RTDMS, Allstom eTerra Vision | Even in real-time applications,voltage stability often requires a long analysis window. Data drop outs can be tolerated and "burst data" packets can be handled by many algorithms.
Thermal Monitoring (Overload) | 0.5 degrees 0.1 p.u. mag | TVE | STD | 0 - 0.2 Hz | STD | 1000 ms | 1 Report/sec | 300 seconds | 30 Reports | X |  | Significant data drop outs can be tolerated and "burst data" packets can be handled by many algorithms. Thermal Monitoring (Overload) is primarily a function of fundamental frequency current and voltages.
Frequency Stability/Islanding | 0.5 degrees 0.01 Hz | TVE | STD | 1.0 - 30.0 Hz | STD | 50 ms | 60 Reports/sec | 5 seconds | 1 Report | P
Remedial Action Schemes: Automatic Arming | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0.02 - 30.0 Hz | STD | 20 ms or 50-70 ms | 1 Report/sec | 300 seconds | 1 Report | P |  | RAS Arming is a low latency, steady state phenomina. The response is based on the overal required timing of the RAS to protect the system from instabllity.
Remedial Action Schemes: Event Detection | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0.02 - 30.0 Hz | STD | 20 ms | 60-120 Reports/sec | 300 seconds | 1 Report | P |  | RAS Event Detection is a low latency, low delay event. Typically it would use a report by exception rather than a polling mechanism. This is only included as a reference NOT a recommended method. RAS event action would be a command action.
Out of step protection | 0.5 degrees 0.01 Hz | TVE | STD | 5.0 - 30.0 Hz | STD | 10 ms | 60 Reports/sec | 5 seconds | 0 Reports | P
Short-term stability control | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0.5 - 30.0 Hz | STD | 16 ms | 60 Reports/sec | 60 seconds | 10 ms | P
Long-term stability control | 0.01 p.u. mag 0.5 degrees | TVE | STD | 0 - 10.0 Hz | STD | 1000 ms | 30 Reports/sec | 600 seconds | 1000 ms | X
FACTS feedback control, Smart switch-able networks | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 1.0 - 30.0 Hz | STD | 16 ms | 60 Reports/sec | 300 seconds | 50 ms | X |  | This is very dependent on the control application. Different objectives would lead to different data reauirements. Voltage Stability would be diffeent the Subsychronus Resonance control.
State Estimation | 0.5 degrees 0.01 Hz | TVE | STD | 0 - 1.0 Hz | STD | 1000 ms | 5 Reports/sec | 300 seconds | 1000 ms | M |  | Assumes traditional static state estimation. Dynamic state estimation would obviously have more stringingent requirements
Disturbance Analysis Compliance | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 30.0 Hz | STD | 1000 ms | 60 Reports/sec | Length of event | 100 ms | M
Frequency Response Analysis | 0.5 degrees 0.01 Hz | TVE | STD | 0 - 1.0 Hz | STD | 1000 ms | 5 Reports/sec | 300 seconds | 25 Reports | M
Model Validation | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 30.0 Hz | STD | 1000 ms | 60 Reports/sec | Time frame of model | 1000 ms | M
Phasor Network performance monitoring & data quality | N/A | TVE | STD | 0 - 30.0 Hz | STD | Measured | 60 Reports/sec | 86400 seconds | 60 Reports | X |  | General evaluation of the phasor communication network, including delays and drop out sensitivities. This application itself is insensitive to drop outs and delays (it is evaluating them), but the results may tie directly into other application requirements.
Baseline Normal Phase Angle Trends | 0.5 degrees | TVE | STD | 0 - 10.0 Hz | STD | 1000 ms | 15 Reports/sec | 86400 seconds | 150 Reports | M
Pattern Recognition/Correlation Analysis | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 0.2 Hz | STD | 1000 ms | 1 Report/sec | 3600 seconds | 20 Reports | M
Situational Awareness Dashboard | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 1.0 Hz | STD | 100 ms | 30 Reports/sec | 300 seconds | 10 Reports | M |  | The data displayed on a trend or visualization may only be updated at 5 times a second or so, but if it is a trend the data should be displayed at scan rate updated at the slower rate.
Real Time Compliance Monitoring with Reliability Standards | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 1.0 Hz | STD | 1000 ms | 5 Reports/sec | 1800 seconds | 10 Reports | M |  | Reports/Second could vary dependent upon the Reliablity standard in question
Real Time Performance Monitoring and Trending | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 0 - 0.2 Hz | STD | 1000 ms | 1 Report/sec | 3600 seconds | 30 Reports | X |  | Not sure what this one means. Are you refering to the Electrical system or the data collection system. Different information would be needed for the different systems.
Anomaly Characterization and Alarming | 0.01 p.u. mag 0.5 degrees 0.01 Hz | TVE | STD | 1.0 - 30.0 Hz | STD | 100 ms | 60 Reports/sec | 3600 seconds | 120 Reports | M
Draft - Updated March 9, 2015 by Frank Tuffner, Pacific Northwest National Laboratory
Contact: francis.tuffner@pnnl.gov
Value contributions from:
Anthony Johnson - Southern California Edison
Unless otherwise noted, values are purely arbitrary and just based on initial guesses
Note on B7: General application class for PMU usage
Note on B8: Modal analysis, oscillation detection
Note on B15: Transient stability
Note on B16: wide area frequency, voltage stability
Note on B26: Angle of separation, voltage and angle profiles, MW and MVAR flows, Load-Resource Imbalance
Note on B28: Real-time alarming on hard limits and "out of normal" conditions, preventive action
Note on C6: Information relating to the characteristics of the measured quantities
Note on C7: Application-specific requirements for the precision on the three base measurement types (magnitude, angle, frequency)
Note on D7: Application-specific requirements for the three base measurement types and the required level of accuracy TVE represents following the C37.118.1-2011 document guidelines
Note on E7: Rate of change of frequency rates the PMU must capture STD represents using the guidance from the IEEE C37.118.1-2011 standard
Note on F7: Range of frequencies the application is examining - represents the frequency content of the sampled phasor values
Note on G7: Required timing accuracy on time stamping process for samples/frames of the PMU data
Note on H6: Characteristics of the data from the PMU to the application location
Note on H7: Delay between the occurrence of an event on the power system and when the packet is finally decoded at the decision or analysis location Similar to "Information transfer time" from IEEE Std 2030-2011
Note on H8: Provided by Anthony Johnson, SCE
Note on H12: Provided by Anthony Johnson, SCE Additional by Bill Wagner - BPA
Note on H13: Provided by Anthony Johnson, SCE
Note on H25: Provided by Anthony Johnson, SCE
Note on I7: Output message rate of data from the PMU
Note on I12: Value provided by Anthony Johnson, SCE
Note on I13: Value provided by Anthony Johnson, SCE
Note on I25: Provided by Anthony Johnson, SCE
Note on J7: Typical interval of data algorithm is analyzing to provide "present" answer
Note on K7: Amount of data loss the application can tolerate before failing. Express as time interval or number of reports corrupted/missed. Caveats on how this missing data can be handled or impact the application can be noted in the Comments section.
Note on L6: General information regarding the application
Note on L7: Expected PMU class for application: M = Measurement P = Protection X = Don't care N = New class (not met)
Note on M7: Example tools or platforms that currently utilize PMU data for this application
Note on N7: Additional comments and caveats
Note on N10: Additional notes/comments provded by Anthony Johnson, SCE
Note on N12: Comments provided by Anthony Johnson, SCE
Note on N13: Comments provided by Anthony Johnson, SCE
Note on N17: Comment provided by Anthony Johnson, SCE
Note on N25: Comment provided by Anthony Johnson, SCE
Note on N26: Comment provided by Anthony Johnson, SCE
Note on N27: Comment provided by Anthony Johnson, SCE