## Sheet1
SITUATIONAL AWARENESS | Application | Latency | Data Resolution | Time Window | Data Requirements | Format /Protocols | Tools/Platforms | Comments
| Situational Awareness Dashboard | 1-5 Seconds | 1 sample/sec. | Snapshot | Phasor, SCADA | PDCStream, IEEE C37.118, OPC, HTTP | PI, RTDMS, PowerWorld, PSGuard | These are summary displays to assess the overall state fo the system (i.e., Normal State, Alert State or Alarm State).
| Real Time Compliance Monitoring with Reliability Standards (Angle of Separation, Voltage & Angle Profiles, MW, MVAR flows, Load-Resource Imbalance) | 1-5 Seconds | 1 sample/sec. | 30 Minutes | Phasor, SCADA | PDCStream, IEEE C37.118, OPC, HTTP | PI, RTDMS, PowerWorld, PSGuard
| Frequency Stability/Islanding | 1-5 Seconds | 30 samples/sec. | Few Minutes | Phasor, FNET | PDCStream, IEEE C37.118 | RTDMS, FNET, StreamReader
MONITORING / ALARMING | Application | Latency | Data Resolution | Time Window | Data Requirements | Format /Protocols | Tools/Platforms | Comments
| Real Time Performance Monitoring and Trending | 1-5 Seconds | 1 sample/sec. | ~ 1 hour | Phasor, SCADA | PDCStream, C37.118, OPC, HTTP | PI, RTDMS | Provide time series information
| Anomaly Characterization and Alarming (Real time alarming on hard limits & "out of normal" conditions, suggest preventive action) | 1-5 Seconds | 30 samples/sec. | ~ 1 hour | Phasor Data | PDCStream, IEEE C37.118, OPC AE | RTDMS, FNET | Alarming points on threshold and rate-of-change violations (either static hard limits based on studies or dynamic soft limits from recent trends and statistics), and suggest appropriate actions.
| State Estimation | 1-2 Minutes | 30 sample/sec. | 5-10 Minutes | Phasor, SCADA, Network Model | PDCStream, IEEE 1344, IEEE C37.118 | ABB, Areva, Siemens | A pilot project between TVA, Entergy and Areva is underway to demonstrate this capability. San Diego Gas & Electric is pursuing a similar project.
| Small-Signal Stability Monitoring | 5-10 Seconds | 10 samples/sec. | 10-15 Minutes | Phasor, FNET | PDCStream, IEEE C37.118 | SCE Outlook, SpectralAnalysis, DSI Toolbox, RTDMS | Tools/Algorithms for small-signal monitoring are specific to the nature of the data: i.e. ambient data, post-event ringdown data, probing data.
| Voltage Stability Monitoring/Assessment | Few Seconds | 30 samples/sec. | ~ 1 hour | Phasor | PDCStream, IEEE 1344, IEEE C37.118, OPC | PSGuard, SynchroWAVe, RTDMS | - Departure from the P-V curve or voltage below limit - Estimation of thevinin equivalent parameters to approximate margins
| Thermal Monitoring (Overload) | Few Seconds | 30 samples/sec. | ~ 1 hour | Phasor, Line Parameters | IEEE 1344, IEEE C37.118 | PSGuard | Current applications require phasor measurements from both ends on the monitored line
ANALYSIS / ASSESSMENT | Application | Latency | Data Resolution | Time Window | Data Requirements | Format /Protocols | Tools/Platforms | Comments
| Baseline Normal Phase Angle Trends | N/A | 1 sample/sec. | 24 hrs + | Phasor, State Estimator | csv, mat, OPC, HTTP, FTP | PI, SQL, DatAWare, Excel, Matlab, RTDMS | Tools with plotting and statistics capabilities are appropriate here.
| Pattern Recognition/Correlation Analysis | N/A | 1 sample/sec. | 1 hour + | Phasor | csv, mat, OPC, HTTP, FTP | PI, SQL, DatAWare, Excel, Matlab | Identify global metrics that look at several parameters to determine system security
| Disturbance Analysis Compliance | N/A | 30 samples/sec. | 1 min pre & 2 min post event | Phasor | PhasorFile (dst), COMTRADE | DSI Toolbox, SCE Outlook, RTDMS
| Frequency Response Analysis | N/A | 10 samples/sec. | 1 min pre & 2 min post event | Phasor, FNET | PhasorFile (dst), csv, mat | Matlab, Excel, PI
| Model Validation | N/A | 30 samples/sec. | 5-10 minutes | Phasor, Model | PhasorFile (dst), csv, mat | Matlab, DSI Toolbox | Simulation tools such as PoweTech's SSAT are needed in conjunction with the PMU measurements
| New Applications Evaluation & Limits Definition | N/A | 30 samples/sec. | Application Depedant | Application Depedant | PDCStream, IEEE C37.118, OPC | TVA SuperPDC, DatAWare, PI
| Email Notification | 1-2 Minutes | 30 samples/sec. | 1 hour | Phasor | Email | Windows Server, SMTP | E-mail transmission of significant events and alerts intended to "get more eyes" in the control room.
| Phasor Network performance monitoring & data quality | N/A | 30 samples/sec. | 24 hrs + | Phasor | PDCStream, IEEE C37.118 | RTDMS, TVA Website, PDCStatus Monitor
ADVANCED APPLICATIONS (PROTECTION & CONTROL) | Application | Latency | Data Resolution | Time Window | Data Requirements | Format /Protocols | Tools/Platforms | Comments
| Automatic Alarming of Remedial Action Schemes | ~ 100 ms | 30 samples/sec. | ~ Minutes | Phasor | IEEE 1344, C37.118 | WACS, PSPM | Research and definion on phasor measurement thresholds for arming/disarming points and tripping criteria
| Out of step protection | ~ 100 ms | 30 samples/sec. | ~ Seconds | Phasor | IEEE 1344, C37.118 | SEL | - Latency consideration are very important
| Short-term stability control (e.g. transient stability) | ~ 100 ms | 30 samples/sec. | ~ Seconds | Phasor | IEEE 1344, IEEE C37.118 | WACS (LabView), PSPM | - Wide Area stability and Voltage Control System (WACS) is presently being used by BPA to validate control concepts
| Long-term stability control (e.g. wide area frequecy, voltage stability) | 1-5 Seconds | 30 samples/sec. | ~ Minutes | Phasor | IEEE 1344, IEEE C37.118 | WACS (LabView), PSPM
| FACTS feedback control, Smart switch-able networks | 1-5 Seconds | 30 samples/sec. | ~ Minutes | Phasor, SCADA | IEEE C37.118 | TBD